## Slide 1: Module 2
Supporting Cabling and Physical Installations

## Slide 2: Module Objectives
Summarize Ethernet standards.
Summarize copper cabling and connector types.
Summarize fiber optic cabling and connector types.
Describe physical installation factors for rack-based installations in server rooms and datacenters.
Deploy and troubleshoot Ethernet cabling.
Notes: The learning objectives align with the following Exam Objectives for Module 2:
  1.5 Compare and contrast transmission media and transceivers.
  2.4 Explain important factors of physical installations.
  5.2 Given a scenario, troubleshoot common cabling and physical interface issues.
  5.5 Given a scenario, use the appropriate tool or protocol to solve networking issues.

## Slide 3: Lesson 2.1
Ethernet
Notes: Suggested Instructional Tip - Ethernet
The main goal of this topic is for students to understand the concepts of media access control and collision domains.
Exam Objectives Covered
  1.5 Compare and contrast transmission media and transceivers.

## Slide 4: Ethernet Standards
IEEE 802.3 standards define the physical layer and data link layer’s media access control (MAC) for wired Ethernet.
Standard | Cables | Speed
10Base-T | Unshielded twisted pair (UTP) | 10 Mbps
100Base-TX Fast Ethernet | Cat5 or higher | 100 Mbps
1000Base-T Gigabit Ethernet | Cat6 or higher | 1000 Mbps
10GBase-T 10 Gigabit Ethernet | Cat6 or higher | 10 Gbps
Notes: Suggested Instructional Tips – Ethernet Standards
The exam tends not to focus too heavily on specific distance limitations, but it encourages students to learn them just in case. Emphasize which standard is applicable to a particular scenario: 100BASE-TX on a legacy network, 10 GbE in a datacenter, and so on.
Notes:
  Ethernet Standards: A foundation for wired network connections
  Key Differentiators:
    Data Transfer Speed: Measured in Megabits per second (Mbps) or Gigabits per second (Gbps) - How fast data travels across the network.
    Cable Type: The specific network cable required for the standard to function.
This table presents a comparison of common Ethernet standards. As you can see, the speed increases significantly as we move from 10BASE-T to 10GBASE-T. The cable type also becomes more sophisticated to support the faster data transfer rates. Applications are also an important consideration. While 10BASE-T is sufficient for basic tasks, 10GBASE-T is ideal for data centers or applications requiring exceptional speed. 100BASE-TX uses twisted-pair copper cables to maintain 100 Mbps speed, while 100BASE-FX offers an option for using fiber optic cables for extended reach at the same speed.
Remember, choosing the right standard depends on your specific needs. Consider the required speed, cable infrastructure, and budget when making your decision.

## Slide 5: Carrier Sense Multiple Access with Collision Detection (CSMA/CD)
Purpose
Process
Carrier Sense
Collision Detection
Resolution
Jam Signal
Backoff Algorithm
Regulates communication in networks with shared transmission mediums
Multiple Access
If two devices transmit simultaneously, a collision is detected.
Notes: Suggested Instructional Tips – Carrier Sense Multiple Access with Collision Detection (CSMA/CD)
  Emphasize the overall principle of media access and contention. Point out that multiplexing is another media access method, but it is more typical of WANs than LANs.
  While CSMA/CD is a bit outdated, explain how it works and point out that related questions will likely be featured in the certification exam. More information about CSMA/CD and wireless technologies is presented later in the course.
Carrier Sense Multiple Access with Collision Detection (CSMA/CD) is a media access control (MAC) method used in Ethernet networks. It essentially dictates how multiple devices share a single cable to transmit data without causing chaos. Here's a breakdown of its key aspects:
Carrier Sense:
  Before transmitting data, a device listens to the network cable to see if it's currently being used by another device. This is like checking if someone is already talking on a walkie-talkie before you try to speak.
  If the cable is free (carrier sense), the device can proceed with sending its data.
  Multiple Access:
  In a CSMA/CD network, multiple devices share the same cable. This means they all have the potential to transmit data at any given time.
  Imagine a classroom where everyone can raise their hand to answer a question, but only one person can speak at a time.
Collision Detection:
  Even after checking the cable, collisions can still happen if two devices attempt to transmit data simultaneously. This is like two people talking over each other at the same time.
  When a collision occurs, both devices detect it and stop transmitting for a random amount of time before retrying. This helps prevent further collisions and ensures data gets sent eventually.

## Slide 6: CSMA/CD Diagram
Notes: Image Description – CSMA/CD Diagram
This slide presents a diagram illustrating the Carrier Sense Multiple Access with Collision Detection (CSMA/CD) protocol. This protocol is used in Ethernet networks to manage data transmission and avoid collisions.
Image Caption:
The CSMA/CD media access method. (Images © 123RF.com.)

## Slide 7: Fiber Ethernet Standards
Standard | Cables | Speed
100Base-FX | MMF (OM1) | 100 Mbps
100Base-SX | MMF (OM1, OM2) | 100 Mbps
1000Base-SX | MMF (OM2, OM3) | 1 Gbps
1000Base-LX | MMF (OM1, OM2, OM3), SMF (OS1, OS2) | 1 Gbps
10GBase-SR | MMF (OM2, OM3, OM4) | 10 Gbps
10GBase-LR | SMF (OS1,OS2) | 10 Gbps
Notes: Suggested Instructional Tips - Fiber Ethernet Standards
  Fiber Optic Advantage: Highlight the primary benefit of Fiber Optic Ethernet - higher bandwidth and longer distances compared to traditional copper-based Ethernet standards.
    Emphasize that fiber optic cables transmit data using light pulses, which travel faster and experience less signal degradation over distance compared to electrical signals in copper cables.
  Standard Specifics: Use the table to explain the key differentiators between the listed Fiber Ethernet standards:
    Speed: Point out the varying data transfer speeds (100 Mbps to 10 Gbps) offered by different standards.
    Cable Types: Introduce the concept of different fiber optic cable types (e.g., Single-mode vs. Multi-mode) used in these standards.
      Briefly explain that Single-mode offers longer reach but requires specialized connectors, while Multi-mode is more common for shorter distances and easier to connect.
    Applications: Discuss the ideal applications for each standard based on speed and distance capabilities.
      For instance, 100Base-SX might be suitable for short-distance, high-bandwidth connections within a building, while 10GBase-LR is suited for long-haul applications between buildings or campuses.
  Beyond the table
    You can mention additional benefits of Fiber Optics like immunity to electromagnetic interference (EMI) which can disrupt copper cables in certain environments.
    Briefly touch upon cost considerations - while fiber optic cabling offers superior performance, it can have a higher initial cost compared to copper.

## Slide 8: Activity: True or False
CSMA/CD regulates communication in networks with shared transmission media.
Notes: Suggested Activity – True or False
Answer: True

## Slide 9: Lesson 2.2
Copper Cables and Connectors
Notes: Suggested Instructional Tips – Copper Cables and Connectors
While students need to know these specifications, you should not need to spend too long on this content in class. Focus on appropriate uses of the different cable types.
Exam Objectives Covered:
1.5 Compare and contrast transmission media and transceivers.

## Slide 10: Unshielded Twisted Pair (UTP)
Structure
Interference
Use
Categories
Installation
Contains 2 to 8 pairs in a plastic jacket
Minimal EMI protection
Popular for LANs because it is cost-effective
Grades like Cat5e (1 Gbps) and Cat6a (10 Gbps)
Avoid sharp bends, keep away from EMI sources
Notes: Suggested Instructional Tips – Unshielded Twisted Pair (UTP)
Explain that twisted pair is very widely deployed as horizontal cabling that links a work area to a patch panel.
  Definition: UTP is a type of cabling that consists of pairs of insulated copper wires twisted together without additional shielding
  Structure: Typically includes 2 to 8 twisted pairs encased in an outer plastic jacket
  Interference: Lacks internal shielding, offering minimal protection against electromagnetic interference (EMI)
  Use: Commonly used for network cabling in LANs due to its low cost, flexibility, and good performance
  Categories: Comes in various grades, such as Cat5e for up to 1 Gbps and Cat6a for up to 10 Gbps
  Installation Tips: Avoid bending sharply and keep away from sources of EMI for optimal performance

## Slide 11: Shielded Twisted Pair Cable (STP)
Structure
Interference
Use
Categories
Installation
Twisted copper wires
Conductive shielding
EMI protection
Reduced crosstalk
High-interference areas
Sensitive data transmission
Grades such as Cat5e, 6, 7
Careful handling
Avoid sharp bends
Notes: Suggested Instructional Tips – Shielded Twisted Pair Cable (STP)
Explain that STP is very widely used to mean any kind of screened or shielded cable, but the actual 150-ohm STP for Token Ring networks is no longer used. F/UTP usually now means Cat 6A cable (though there are older 5e and 6 varieties), while S/FTP usually means Cat 7 or Cat 8.
  Structure:
    Twisted Copper Wires: Pairs of insulated copper wires twisted together.
    Conductive Shielding: Each pair wrapped in foil or braided shield.
Interference:
    EMI Protection: Shields block external electromagnetic interference.
    Reduced Crosstalk: Twisting reduces signal interference between pairs.
Use:
    High-Interference Areas: Ideal for environments with heavy electrical noise.
    Sensitive Data Transmission: Preferred for secure or private network installations.
Categories:
    Performance Grades: Available in Cat5e, Cat6, Cat7, etc., for varying speeds and frequencies.
Installation:
    Careful Handling: Shielding must be grounded properly to be effective.
    Avoid Sharp Bends: To maintain cable integrity and performance.

## Slide 12: Ethernet Connectors
Feature | RJ11 | RJ45
Image |  | 
Configuration | 6 positions, 4 connectors | 8 positions, 8 connectors
Usage | Phone and modem | Computer networking
Bandwidth | 24 Mbps | 10 Gbps over Ethernet
Notes: Suggested Instructional Tip - Ethernet Connectors
RJ45 plugs have a plastic retaining clip. This is normally protected by a rubber boot. This type of cable construction is also referred to as snagless.
There are also GG45 and TERA connectors, associated with ISO Class F and Class II cabling. GG45 has a similar form factor to RJ45 but has four conductors in the corners. TERA connectors have a completely different form factor.

## Slide 13: Plenum and Riser-Rated Cable
Plenum-rated
Riser-rated
Installed in plenum spaces
Made of fire-resistant low toxic materials
Meets higher fire safety standards
More expensive
Used in vertical spaces between floors
Fire-resistant
Prevent the spread of fire between floors
More cost-effective
Notes: Suggested Instructional Tip - Plenum and Riser-Related Cable
Plenum-Rated Cable (CMP):
    Usage: Installed in plenum spaces (a void in a building designed to carry heating, ventilation, and air conditioning (HVAC) systems) used for air circulation in HVAC systems.
    Material: Made of materials like PVC or FEP that are fire-resistant and emit fewer toxic fumes.
    Safety: Meets higher fire safety standards due to the potential of air circulation spreading smoke.
    Cost: Generally, more expensive due to the higher material and safety standards.
Riser-Rated Cable (CMR):
    Usage: Used in vertical spaces (risers) that run between floors to distribute utilities.
    Material: Fire-resistant but not to the same degree as plenum-rated cables.
    Safety: Designed to prevent the spread of fire between floors, less stringent than plenum requirements.
    Cost: More cost-effective than plenum-rated cables.
Key Points:
    Plenum-rated cables are necessary for spaces where air is recirculated throughout a building.
    Riser-rated cables are suitable for vertical runs in non-plenum spaces.
    Both types are flame-retardant, but plenum cables have stricter fire resistance due to their location in airflow spaces12.
    A plenum cable can be used in a riser space, but a riser cable generally cannot be used in a plenum space3.

## Slide 14: Coaxial and Twinaxial Cable
Feature | Coaxial | Twinaxial
Image |  | 
Configuration | Central conductor, insulation, metallic shield, outer jacket | Two inner conductors in a twisted pair, insulation, outer jacket
Usage | TV, Internet, radio signals, CCTV | 10 GB Ethernet networks
Bandwidth | Wide range of frequencies, high-speed data transmission | Very-short range high-speed
Connectors | BNC, TNC, SMA | Proprietary
Notes: Suggested Instructional Tip
Inform students that coax is not widely deployed except in CATV and datacenters (twinax). The RG specification codes come from their page numbers in the Radio Guide manual, the original military specification (Mil-Spec) for coax cables, which is no longer in use.
Image (left) caption:
Direct Attach Copper (DAC) twinax cabling with SFP+ termination. (Image created by Labsy and reproduced under the Creative Commons Attribution ShareAlike 4.0 license.)
Image (right) caption:
Coax cable. (Image by destinacigdem © 123RF.com.)

## Slide 15: Activity: Multiple Choice
What would be the best cable to use?
Unshielded Twisted Pair (UTP)
Shielded Twisted Pair (STP)
Coaxial Cable
Fiber Optic Cable
A company is setting up a network in an industrial environment where machinery often causes significant electromagnetic interference.
The network requires a cabling solution that can handle high-speed data transfer while also being resistant to this interference. The cable will be used to connect servers, and the runs will not exceed 100 meters.
Notes: Suggested Activity – Multiple Choice
Correct answer: B. Shielded Twisted Pair (STP)
Explanations
Unshielded Twisted Pair (UTP)
    Though affordable and commonly used, UTP's lack of shielding makes it unsuitable for environments with significant EMI.
**Shielded Twisted Pair (STP)
    Electromagnetic Interference (EMI) Resistance: The question specifies significant EMI from machinery. UTP cables are susceptible to EMI, which can disrupt data transmission. STP offers a metal braid shielding that significantly reduces the impact of EMI, making it a more reliable choice in this environment.
    High-Speed Data Transfer: While not quite reaching the performance of fiber optics, STP can handle high-speed data transfer within data centers. It can support Gigabit Ethernet and even 10 Gigabit Ethernet for shorter distances (like the 100 meters mentioned in the question).
    Cost-Effectiveness: Compared to fiber optic cables, STP offers a more cost-effective solution, especially for shorter distances within a data center.
    Distance Limitation: The question specifies cable runs not exceeding 100 meters. While both STP and fiber optics can handle this distance, fiber becomes less cost-effective for shorter runs.
Coaxial Cable
    While offering some EMI protection, coaxial cables are generally thicker and less flexible than STP, making them less ideal for data center applications.
Fiber Optic Cable
    Provides the highest immunity to EMI and excellent data transfer speeds. However, for shorter data center runs (under 100 meters), the cost and complexity of installation might not be justified compared to STP.

## Slide 16: Lesson 2.3
Wiring Implementation
Notes: Suggested Instructional Tips – Wiring Implementation
Interaction Opportunity
Because of the difficulty in specifying equipment, there are no specific hardware activities in this topic. Students would benefit from hands-on experience of wiring a patch panel and wall plates (and to a lesser extent crimping patch cords or creating a crossover cable).
If you have the facilities and tools available in your training center, then leading students through a hands-on activity is recommended. Alternatively, if you can arrange it, visit the telecommunications room in your facility so that students can observe the cabling.
Exam Objectives Covered
2.4 Explain important factors of physical installations.

## Slide 17: Structured Cabling System
Work Area
User connection point
Horizontal Cabling
Floor-level networking
Multiple intermediate distribution frames (IDFs)
Telecommunications Room
Equipment hub
Dedicated space
Backbone Cabling
Vertical connections
Entrance Facilities/Demarc
Network transition point
Local exchange carrier (LEC) integration
Houses an IDF
Connects IDFs to a main distribution frame (MDF)
A structured cabling scheme is a standard way of provisioning cabled networking for computers in an office building.
Notes: Suggested Instructional Tip - Structured Cabling System
Work Area:
User Connection Point: Where devices connect to the network via patch cables and wall ports.
Horizontal Cabling:
  Floor-Level Networking: Links work areas to an Intermediate Distribution Frame (IDF) within 90 meters.
  Multiple IDFs: Used when a single IDF can’t serve all areas due to distance limitations.
Telecommunications Room:
  Equipment Hub: Houses IDFs and networking equipment like switches.
  Dedicated Space: Reserved solely for networking, not general storage.
Backbone Cabling:
  Vertical Connections: Runs between floors, linking IDFs to the Main Distribution Frame (MDF).
Entrance Facilities/Demarc:
  Network Transition Point: Where external and internal cabling meet at the MDF.
  LEC Integration: Connects the building to the local exchange carrier’s network.

## Slide 18: Structured Cabling Diagram
Notes: Suggested Instructional Tips – Structured Cabling Diagram
Run through the elements of the TIA wiring distribution scheme.
Image Caption:
Wiring distribution components. (Images © 123RF.com.)
Image Description:
The components are telecommunication closet, horizontal cabling, work areas, backbone cabling, equipment room, access provider's cabling, modem or demarc, and entrance facilities.

## Slide 19: T568A and T568B Termination Standards
Notes: Suggested Instructional Tips – T568A and T568B Termination Standards
Encourage students to memorize these wiring configurations.
T568A Termination Standard:
    Wire Arrangement: Green and orange pairs are in different positions compared to T568B.
    Backward Compatibility: Recommended for residential installations for compatibility with older technology like fax machines
    Government Use: Sometimes specified in U.S. government contracts
T568B Termination Standard:
    Wire Arrangement: Orange pair is in pins 1 and 2, green in pins 3 and 6, which is different from T568A.
    Common Use: Preferred for most installed telecom infrastructures and current Ethernet applications
    Noise Protection: Offers better protection from noise and isolates signals more effectively than T568A
Image Description:
RJ-45 connector EIA or TIA 568A standard and RJ-45 connector EIA or TIA 568B standard have eight pins and four wire pairs, each.
Image Caption:
T568A and T568B wiring diagrams. (Images © 123RF.com.)

## Slide 20: Patch Panels
Purpose
Structure
Function
Wiring Standards
Facilitates cable management
Punch down blocks at rear for cable termination
RJ45 ports in front for device connections
IDC terminals allow for secure and compact cable termination
RJ45 ports enable easy reconfiguration of network connections
Supports T568A wiring schemes
Supports T568B wiring schemes
Notes: Suggested Instructional Tips – Patch Panels
If possible, provide examples of wiring blocks that the students can pass around and examine.
Patch panels are typically mounted in network closets or server rooms and are an integral part of the LAN infrastructure, providing a centralized point for all network cables. They are designed to accommodate a variety of cable types and are essential for maintaining a tidy and functional network environment.
Image Caption:
IDCs at the rear of a patch panel. (Image by plus69 © 123RF.com.)

## Slide 21: Patch Panels
Notes: Suggested Instructional Tips – Patch Panels
If possible, provide examples of wiring blocks that the students can pass around and examine.
Patch panels are typically mounted in network closets or server rooms and are an integral part of the LAN infrastructure, providing a centralized point for all network cables. They are designed to accommodate a variety of cable types and are essential for maintaining a tidy and functional network environment.
Image Caption:
IDCs at the rear of a patch panel. (Image by plus69 © 123RF.com.

## Slide 22: Structured Cable Installation
Preparation
Pulling Cable
Termination
Connection
Testing
Documentation
Gather tools
Plan route
Label cables
Route cables
Bundle cables
Service loop
Cut and label
Patch panel
Work area
Verify connections
Test network
Record details
Notes: Suggested Instructional Tip - Structured Cable Installation
Preparation:
    Gather Tools: Obtain necessary tools like electrician’s scissors, cable strippers, and labels.
    Plan Route: Determine the path from the telecommunications closet to the work area, avoiding electrical interference sources.
Pulling Cable:
    Label Cable: Mark the cable end with the jack ID before pulling.
    Route Cable: Carefully pull the cable through conduits or wall spaces, ensuring no excessive bends.
    Bundle Cables: Group multiple cables if they share a destination to streamline the process.
Termination:
    Service Loop: Leave extra cable at both ends for future adjustments.
    Cut and Label: Trim the cable to the needed length and label the other end with the corresponding ID.
Connection:
    Patch Panel: Connect the cable to the patch panel using the punch down tool.
    Work Area: Run the cable to the work area outlet and secure it.
Testing:
    Verify Connections: Ensure all cables are correctly terminated and seated.
    Test Network: Use a cable tester to check for continuity and proper signal transmission.
Documentation:
    Record Details: Document the cable runs, IDs, and any other relevant information for maintenance and troubleshooting.

## Slide 23: Termination Tools
Cable Cutters
Crimp Tools
Punch-Down Tools
Cable Strippers
For clean cuts of the cable without damaging wires.
To attach connectors to the cable ends.
For terminating cable wires in punch down blocks.
For safely removing insulation without nicking wires.
Notes: Suggested Instructional Tip – Termination Tools
If possible, provide examples of termination tools that the students can pass around and examine.
Note:
To terminate a cable, untwist the ends of the wire pairs and place them into the punch down block in the correct order for the wiring configuration (T568A or T568B) you want to use.
You must not untwist the wires too much. Cat 6 is demanding in this respect and requires no more than 0.375" (1 cm) of untwisting.

## Slide 24: Activity: Identify the Termination Tool
1
2
3
4
Notes: Suggested Activity – What is it?
Wire stripper
Crimping tool
Punch down tool
Cable cutter

## Slide 25: Lesson 2.4
Fiber Optic Cables and Connectors
Notes: Suggested Instructional Tip – Fiber Optic Cables and Connectors
Fiber optic cabling installation tends to be performed by specialists, but be sure to explain deployment considerations, such as the type and grade of cable to use plus suitable connectors.
Exam Objectives Covered
1.5 Compare and contrast transmission media and transceivers.
2.4 Explain important factors of physical installations.

## Slide 26: Fiber Optic Considerations
Fiber optic cables
Composition
Benefits
Thin stands of glass or plastic
Transmit data using light pulses
Core: ultra-pure strands of glass or plastic
Cladding: reflects light back into the core
Buffer: outer protective jacket
Transmit data up to 400 Gbps
Maintain signal quality over long distances
Immune to electromagnetic interference
Notes: Suggested Instructional Tips – Fiber Optic Considerations
Fiber optic is used on LANs for backbone cabling and is widely deployed on telecommunications networks and within datacenters.
Fiber Optic Cable Construction:
Imagine thin strands of glass or plastic – that's the essence of a fiber optic cable! These strands, called the core, are the path for light pulses to travel and carry data.
Core: Made of ultra-pure glass or plastic, it guides the light pulses with minimal signal loss.
Cladding: This layer surrounds the core. It's made of a material with a slightly lower refractive index than the core, causing light to reflect back into the core instead of escaping. This ensures efficient light transmission.
Buffer: The outermost layer provides physical protection for the core and cladding. It's typically a flexible material like plastic to withstand bends and external pressure.
Benefits of Fiber Optic Cables:
Unmatched Speed: Fiber optic cables can transmit data at blazing-fast speeds, currently reaching up to a staggering 400 Gigabits per second (Gbps). This is significantly higher compared to traditional copper cables.
Long-Distance Champion: Unlike copper cables that experience signal degradation over distance, fiber optics can maintain strong signal quality for kilometers. This makes them ideal for connecting buildings, campuses, or even cities with minimal data loss.
EMI Immunity: Electromagnetic interference (EMI) from electrical devices can disrupt data transmission in copper cables. Fiber optic cables, however, are immune to EMI because they transmit data using light pulses, not electrical signals. This ensures reliable data transfer even in noisy industrial environments.
Additional Points:
Briefly mention different types of fiber optic cables (Single-mode vs. Multi-mode) and their suitability for various distances.
Touch upon the cost factor – while offering superior performance, fiber optic cabling can have a higher initial cost compared to copper. However, the long lifespan and low maintenance needs can offset the initial investment in the long run.

## Slide 27: Single Mode and Multimode Fiber
Factor | Single Mode | Multimode
Core diameter | Small core allowing only one light to pass through | Larger core allowing multiple light modes to pass through
Light transmission | Light travels directly down the fiber with minimal reflection and attenuation | Light bounces more causing more dispersion and attenuation
Distance and bandwidth | Suitable for long distances | Best for shorter distances
Applications | Long-haul networks, high-speed broadband, telecommunications | Datacenters, LANs
Cost | More expensive | Less expensive
Notes: Suggested Instructional Tips – Single Mode and Multimode Fiber
Point out that SMF is required for long-distance links. For shorter links, there is a choice between MMF and SMF. Historically, MMF was widely used because it uses cheaper optical transceivers. That price differential is now much less, meaning that SMF is increasingly popular for short-range datacenter applications.
Note:
Optical transceivers for SMF are now only slightly more expensive than ones for MMF. Consequently, SMF is often used for short-range applications in datacenters, as well as for long-distance links. SMF still comes at a slight price premium, but it provides better support for 40 Gbps and 100 Gbps Ethernet standards.

## Slide 28: Fiber Optic Connector Types
Factor | Subscriber Connector (SC) | Lucent Connector (LC) | Straight Tip Connector (ST)
Image |  |  | 
Ferrule Size | 2.5 mm | 1.25 mm | 2.5 mm
Applications | Telecommunications networks, data transmission | Heavily populated patch panels and cabinets | LANS and datacenters
Features | Push-pull design, quick deployment, low insertion loss, durability | Square shape, duplex header design | Bayonet twist-lock, older but still widely used
Notes: Suggested Instructional Tip - Fiber Optic Connector Types
Straight Tip (ST) Connector (Refer to slide image)
Description: The granddaddy of fiber optic connectors, the ST connector has a cylindrical metal housing with a bayonet locking mechanism.
Pros: Simple and durable design, well-suited for harsh environments.
Cons: Larger size compared to newer connectors, less common in modern data center applications.
Subscriber Connector (SC) Connector (Refer to slide image)
Description: A popular choice, the SC connector features a square-shaped plastic housing with a push-pull locking mechanism.
Pros: Compact design, easier to use than ST connectors, widely available.
Cons: Not ideal for high-density applications due to its square shape.
Local Connector (LC) Connector (Refer to slide image)
Description: The LC connector is a miniature version of the SC connector, boasting a rectangular plastic housing with a push-pull locking mechanism.
Pros: Smallest of the three, ideal for high-density installations in data centers due to its compact size.
Cons: More delicate design compared to ST connectors, might require more care during handling.

## Slide 29: Wavelength Division Multiplexing (WDM)
Bidirectional WDM (BiDi):
Supports Tx and Rx over the same fiber strand
Uses shifted wavelengths (1310 nm for Tx, 1490 nm for Rx)
Requires installation in opposite pairs
Documented in Ethernet standards (1000BASE-BX, 10GBASE-BX)
Coarse WDM (CWDM):
Supports up to 16 wavelengths
Typically used for 4-8 bidirectional channels on a single strand
Can also be used for unidirectional channels on dual strands
Dense WDM (DWDM):
Provisions more channels (20, 40, 80, or 160)
Requires precise lasers due to less spacing between channels
Supports multi-channel 1G, 10G, and 40G Ethernet links
Transceivers installed in opposite pairs for proper function
Allows multiple data channels to share the same fiber using different wavelengths of light
Notes: Suggested Instructional Tip - Wavelength Division Multiplexing (WDM)
Fiber optic cables provide incredible bandwidth for transmitting information. But what if we could squeeze even more data through a single fiber? That's the benefit of Wavelength Division Multiplexing (WDM): WDM allows us to transmit multiple data streams simultaneously on a single fiber optic cable, using different colors of light.
Breaking Down WDM:
Imagine a highway with multiple lanes. WDM is like taking advantage of those lanes to send different data streams concurrently on a single fiber optic cable.
Instead of lanes, WDM uses different wavelengths of light to carry separate data streams. Each wavelength acts like a virtual lane on the fiber optic cable.
Types of WDM Systems
BiDi WDM: utilizes separate wavelengths for transmission and reception. This allows for full-duplex communication, where data can flow in both directions on a single fiber optic cable.
Coarse Wavelength Division Multiplexing (CWDM): Uses wider channel spacing, making it simpler and more affordable. Ideal for shorter distances and lower data capacity requirements.
Dense Wavelength Division Multiplexing (DWDM): Utilizes narrower channel spacing, enabling more channels on a single fiber. Perfect for high-capacity, long-distance networks.

## Slide 30: Activity: Two Truths and a Lie
Fiber optic cables are made of thin strands of glass or plastic that transmit data using light pulses
Single mode fiber causes more dispersion and attenuation then multimode fiber
Lucent connectors are often used for heavily populated patch panels
Notes: Suggested Activity – Two Truths and a Lie
LIE: Single mode fiber causes more dispersion and attenuation than multimode fiber.
Dispersion: Multimode fiber suffers from a phenomenon called modal dispersion. Light travels through the larger core of multimode fiber in multiple paths (modes). These modes arrive at the receiving end at slightly different times, causing the signal to spread and weaken (dispersion). Single-mode fiber, with its smaller core, allows only one mode of light propagation, minimizing modal dispersion and keeping the signal strong and well-defined.
Attenuation: Attenuation refers to the loss of signal strength as it travels through the fiber. While both types experience attenuation, single-mode fiber generally exhibits lower attenuation compared to multimode fiber, especially at longer distances. This is because the smaller core in single-mode fiber reduces light scattering and absorption within the cable.
Therefore, single-mode fiber is the preferred choice for high-bandwidth, long-distance applications where minimizing signal degradation is critical. Multimode fiber, while easier to work with due to its larger core size, is more suited for shorter distances and lower-bandwidth applications where cost might be a bigger factor.

## Slide 31: Lesson 2.5
Physical Installation Factors
Notes: Exam Objectives Covered
2.4 Explain important factors of physical installations.

## Slide 32: Rack Systems
Secure Areas
Telecommunications closets, equipment rooms, server rooms
Datacenters for server provisioning
Access Control
Physical access controls for authorized entry
Rack Installation
Steel shelving systems for standard-size equipment
Secure, compact storage; increased density
Standard Sizing
EIA standard 19"/48.26 cm width for rack-mounting
Notes: Suggested Instructional Tip - Rack Systems
Secure Installation Areas:
  Equipment should be in secure areas like telecommunications closets, equipment rooms, or server rooms.
  A dedicated facility for servers is known as a datacenter.
  These spaces are exclusively for technology equipment, not for general storage.
Access Control:
  Physical access controls are necessary to ensure only authorized personnel can enter these areas.
Rack Installation:
  Equipment is installed in racks, which are steel shelving systems designed for standard-size equipment.
  Racks provide secure and compact storage, increasing the density of computing appliances.
Standard Sizing:
  Network appliances and server hardware are designed for EIA standard 19" / 48.26 cm rack-mounting.
  Standard components are screwed directly into the rack.
Nonstandard Components:
  Items like tower servers or monitors can be installed on shelves within the racks.

## Slide 33: Humidity and Temperature
Temperature Monitoring
Prevents overheating
Ensures effective heat dissipation
Humidity Control
Avoids condensation and corrosion
Reduces static charge risks
Electrical Stability
Ensures uninterrupted power supply
Monitors for voltage irregularities
Flood Detection
Identifies water-related risks
Triggers immediate system shutdowns
Notes: Suggested Instructional Tip - Humidity and Temperature
Servers and appliances are fitted with internal sensors to monitor conditions within the device chassis. These can report problems such as excessive temperatures within the device chassis, fan speeds, component failure, and chassis intrusion to a monitoring system.

## Slide 34: Power Management
34
Power Essentials
Essential stable power for network appliances
Protection against voltage spikes, surges, and failures
Load and Voltage
AC circuits aligned with equipment load
High-voltage circuits in datacenters
PDUs
Ensure clean power signals
Offer remote monitoring/ control
Battery Backups
Component-level storage device protection
UPS for system-level power continuity
UPS runtime dependent on load/model
Notes: Suggested Instructional Tip - Power Management
Power Essentials:
  Stable power supply is crucial for all network appliances.
  Voltage spikes, surges, under-voltage events, and power failures can cause equipment crashes or failures.
Load and Voltage:
  AC circuits supplying power must match equipment load capacity.
  High-voltage circuits (e.g., 240 VAC) are common in datacenters.
Power Distribution Units (PDUs):
  Clean power signals, protect against events.
  Remote monitoring and control options.
Battery Backups:
  Component-level backup for storage devices.
Uninterruptible Power Supplies (UPS)
  Sustain system operation during power loss.
  UPS runtime varies based on load and model.

## Slide 35: Fire Suppression
Fire Safety Elements
Clearly marked fire exits
Regular emergency evacuation drills
Fire-resistant building design
Detection and Alarms
Automatic and manual smoke/fire detection systems
Extinguishers
Various types for different fire classes
Class C extinguishers for electrical safety
Sprinkler Systems
Heat-triggered, water discharge
Risk of burst pipes, accidental triggering
Sprinkler Alternatives
Dry-pipe
Pre-action
Halon (phased out)
Clean agent
Notes: Suggested Instructional Tip - Fire Suppression
Fire Safety Elements:
  Clearly marked fire exits.
  Regular emergency evacuation drills.
  Fire-resistant building design.
Detection and Alarms:
  Automatic and manual smoke/fire detection systems.
Extinguishers:
  Various types for different fire classes.
  Class C extinguishers for electrical safety.
Sprinkler Systems:
  Wet-pipe: Heat-triggered, water discharge.
  Risks: Burst pipes, accidental triggering.
Sprinkler Alternatives:
  Dry-pipe: For areas at risk of freezing.
  Pre-action: Fills with water upon alarm, sprays with heat.
  Halon: Non-residue, ozone-depleting (phased out).
  Clean agent: Environmentally safe, non-toxic (e.g., INERGEN, FM-200).

## Slide 36: Activity: Prevention
How would you…
Prevent equipment from overheating in a server room?
Prevent static discharge?
Protect equipment and data from under-voltage events?
Notes: Suggested Activity - Prevention
Prevent Equipment from Overheating:
Maintain Proper Airflow: Ensure there are no obstructions blocking air vents in server racks or throughout the room. Regularly clean air filters in cooling systems for optimal airflow. Consider strategic placement of server racks to avoid creating hot spots. Explore options like adding ceiling fans or strategically placed fans to improve air circulation.
Monitor Temperature: Implement temperature monitoring systems to track server room temperature and identify potential overheating zones. Set up alerts to notify you if temperatures exceed safe operating ranges.
Optimize Cooling Systems: Ensure air conditioners or dedicated server cooling units are functioning properly and sized appropriately for the heat load in the room. Consider preventive maintenance for cooling systems to maintain efficiency.
Physical Measures: In extreme cases, investigate options like raising the floor for better air circulation or using specialized cooling doors for server racks.
Prevent Static Discharge (ESD):
Grounding: Implement a proper grounding system throughout the server room. This includes grounding server racks, equipment chassis, and ESD mats at workstations. Ensure personnel wear ESD wrist straps when handling sensitive electronic components.
Humidity Control: Maintain a moderate level of humidity (around 40-60%) in the server room. Very dry environments can increase the risk of static buildup. Consider using humidifiers if needed.
Flooring: Use anti-static flooring materials to dissipate static charges and reduce the risk of ESD events. Regularly clean and maintain the flooring to ensure its effectiveness.
Training: Train personnel on proper handling procedures for electronic components to minimize the risk of accidental static discharge.
Protect Equipment and Data from Under-Voltage Events:
Uninterruptible Power Supply (UPS): Implement a UPS system to provide backup power in case of power outages or voltage fluctuations. Choose a UPS with appropriate capacity to support your server room equipment for the desired runtime during an outage. Regularly test and maintain the UPS system to ensure its functionality.
Surge Protectors: Utilize surge protectors for sensitive equipment to guard against sudden voltage spikes that can damage hardware.
Data Backup and Recovery: Implement a robust data backup and recovery plan. Regularly back up your critical data to a secure offsite location to ensure data integrity in case of a disaster. Test your backup and recovery procedures regularly to ensure they function as expected.
Power Monitoring: Consider using power monitoring systems to track power fluctuations and identify any potential power quality issues.

## Slide 37: Lesson 2.6
Cable Troubleshooting
Notes: Suggested Instructional Tip – Cable Troubleshooting
As well as presenting the individual scenarios and tools, try to reinforce application of the troubleshooting model as you work through this topic.
Exam Objectives Covered
5.2 Given a scenario, troubleshoot common cabling and physical interface issues.
5.5 Given a scenario, use the appropriate tool or protocol to solve networking issues.

## Slide 38: Specifications and Limitations: Speed vs. Throughput
Physical layer
Symbols: events like voltage pulses or wave transitions
Data Link Layer
Nominal bit rate: information transmitter per second
Ethernet: expected performance (10 Mbps, 100 Mbps, 1 Gbps, etc.)
Throughput
Average data transfer rate over time
Goodput: Averaged data transfer rate at Application layer
Baud rate: symbols per second (measured in Hz, MHz, GHz)
Encoding methods: higher bit rate than baud rate
Latency (speed): time unit (ms), also referred to as delay
Notes: Suggested Instructional Tips – Specification and Limitations: Speed vs. Throughput
Physical Layer:
  Symbols: Think of symbols as cars on a highway. Each car represents a symbol.
  Baud Rate: The number of cars passing a point per second. This is like counting how many cars pass a toll booth in one second.
Data Link Layer:
  Nominal Bit Rate: This is like the maximum speed limit of the highway (e.g., 60 mph). It represents the potential speed at which cars can travel.
  Encoding Methods: Imagine each car carrying multiple passengers. More passengers per car mean more information is being transported efficiently.
  Ethernet: Different highways have different speed limits (10 mph, 100 mph, 1,000 mph, etc.).
Throughput:
  Average Data Transfer Rate: This is like the actual average speed of cars on the highway over time, considering traffic, accidents, and road conditions.
  Goodput: This is like measuring how many passengers actually reach their destination without delays (accounting for lost or delayed cars).
  Latency (Speed): The time it takes for a car to travel from one point to another (measured in milliseconds). This is also referred to as delay.

## Slide 39: Specifications and Limitations
Distance limitations
Media types support specific bit rates over defined distances
Attenuation
Loss of signal strength (dB) Ratio of signal strength at origin vs. destination
Interference (Noise)
Unintended signals within or near the channel Causes errors and retransmissions Expressed as Signal to Noise Ratio (SNR)
Notes: Suggested Instructional Tips – Specification and Limitations: Distance Limitations, Attenuation, and Interference
Distance Limitations:
  Different highways can support different speeds over various distances.
  Attenuation:
  Imagine the cars losing fuel as they travel. The further they go, the more fuel they lose, which slows them down (loss of signal strength).
Interference (Noise):
  Think of interference as road construction or bad weather. It makes it harder for cars to travel smoothly, causing delays and accidents (errors and retransmissions).

## Slide 40: Cable Issues: Symptoms
Slow Internet speeds
Connection timeouts
Slowing down of applications
Frequent drops or unstable network link
Random disconnections and reconnections
Lagging audio/video communication
Notes: Suggested Instructional Tip - Cable Issues: Symptoms
Slow Internet Speeds: This can be caused by:
  Cable type limitations: Using a cable type not rated for your desired speed (e.g., Cat5 for Gigabit Ethernet).
  Excessive cable length: Signal degradation over long distances can reduce achievable speeds.
  Physical damage: Cuts, crimps, or bends in the cable can weaken the signal.
  Random Disconnections and Reconnections: This could be due to:
  Loose or faulty connectors: Ensure connectors are securely fastened and not damaged.
  Cable quality issues: Low-quality cables might be more prone to connection drops.
  Interference: Electrical noise from nearby devices can disrupt cable signals.
  Connection Timeouts: Similar to disconnection issues, timeouts can be caused by:
  Cable problems: Signal weakness or intermittent disruptions can lead to timeouts.
  Network congestion: Heavy traffic on the network can cause delays and timeouts.
  Slowing Down of Applications: This can be a symptom of:
  Overall network slowdown: Underlying cable issues might contribute to sluggish network performance impacting applications.
  Insufficient cable bandwidth: For bandwidth-intensive applications, a cable might not be able to handle the data demands.
  Lagging Audio/Video Communication: This often occurs due to:
  Packet loss: Damaged cables can cause data packets to be lost during transmission, resulting in choppy audio or video.
  High latency: Delays in data transfer over a compromised cable can lead to lagging communication.
  Frequent Drops or Unstable Network Link: This indicates potential issues like:
  Intermittent cable faults: The cable might have internal damage causing sporadic signal disruptions.
  Connectivity problems: Issues with the cable connection points at either end could lead to frequent drops.

## Slide 41: Cable Issues: Troubleshooting
Physical inspection of cables
Substitute patch cords with known good ones if faulty
Test transceivers with a loopback tool
Use alternative hosts or switch ports to test connectivity
Check structured cabling with appropriate tools
Verify drivers and network adapter
Verify patch cord connections
Notes: Suggested Instructional Tip - Cable Issues: Symptoms
Physical Inspection of Cables: Emphasize the importance of visually inspecting cables for any obvious signs of damage, such as cuts, frays, or kinks. Mention that physical damage can cause connectivity issues and should be addressed immediately. Encourage learners to look for loose or improperly seated connectors. Suggest checking for any environmental factors that might affect the cables, such as exposure to heat or moisture.
Verify Patch Cord Connections: Explain that verifying patch cord connections ensures that all cables are securely connected to the correct ports. Suggest double-checking both ends of the patch cords to ensure they are properly plugged in. Recommend labeling cables to avoid confusion and ensure correct connections.
Substitute Patch Cords with Known Good Ones if Faulty: Highlight the importance of using known good patch cords to replace potentially faulty ones. Encourage learners to keep a set of tested and verified patch cords for troubleshooting purposes. Suggest marking faulty cables to avoid reusing them in the future.
Test Transceivers with a Loopback Tool: Describe how a loopback tool can be used to test transceivers by looping the signal back to the device to verify functionality. Demonstrate how to use a loopback tool and interpret the results. Explain that a successful loopback test indicates that the transceiver is functioning correctly.
Use Alternative Hosts or Switch Ports to Test Connectivity: Explain that using alternative hosts or switch ports can help isolate the issue by determining if the problem is with the original host or port. Suggest swapping the cable to a different port on the switch or connecting it to a different host to see if the issue persists. Recommend documenting the results to identify patterns or recurring issues.
Check Structured Cabling with Appropriate Tools: Highlight the importance of using appropriate tools, such as cable testers or certifiers, to check the integrity of structured cabling. Demonstrate how to use a cable tester to check for continuity, shorts, and other issues. Explain the importance of following industry standards for structured cabling.
Verify Drivers and Network Adapter: Emphasize the need to verify that the drivers and network adapter are functioning correctly and are up to date. Suggest checking the device manager or network settings to ensure the network adapter is recognized and functioning. Recommend updating drivers to the latest version provided by the manufacturer.

## Slide 42: Cable Testers
Diagnosis with Cable Testing Tools
Used when cable is not directly accessible
Diagnose intermittent connectivity or performance issues
Cable Tester Functions
Reports on physical and electrical properties
Tests conditions, crosstalk, attenuation, noise, resistance
Notes: Suggested Instructional Tip - Cable Testers
Cable testing tools can be used for troubleshooting and verification. It is best to verify wiring installation and termination just after you have made all the connections. This means you should still have access to the cable runs. Identifying and correcting errors at this point will be much simpler than when you are trying to set up end user devices.

## Slide 43: Wire Map Testers and Tone Generators
Wire Map Testers
Detect improper cable termination
Use base and remote units to test each wire conductor
Identify issues like open circuits, shorts, and incorrect pin-outs
Tone Generators
Trace cables through walls or identify active cables in a bundle
Known as “Fox and Hound”
Apply signal to trace cable with a probe
Notes: Suggested Instructional Tip – Wire Map Testers and Tone Generators
Emphasize the different tests that can be performed by a wire map tester.
Wire Map Testers:
  Identify the continuity, shorts, and opens in wire and cable configurations. Map the wiring sequence (pin-out) of a cable to ensure proper connections at both ends. Commonly used for troubleshooting network cabling (coaxial, twisted-pair), phone lines, and other low-voltage wiring systems.
  Demonstrate proper usage, including connecting the tester to the cable and interpreting the results (lights, beeps, or on-screen displays). Explain different types of wire map testers (basic continuity testers with LEDs or beeps to indicate connection status and advanced testers with LCD screens that display detailed wire map information and can identify cable type and potential faults like crosstalk).
  Emphasize their importance in ensuring proper network and communication system installation and maintenance. Highlight how they help troubleshoot connection issues, identify cable faults, and verify wiring configurations.
  Mention limitations like not always pinpointing the exact location of a fault within a cable. They might require some familiarity with wiring standards and cable types for accurate interpretation of results.
Tone Generators
  Emit a specific audible tone along a cable. Used in conjunction with a probe on a wire map tester to identify the corresponding cable at the other end. Helpful for tracing cables hidden within walls, ceilings, or bundles.
Highlight different types of tone generators: standalone units or integrated into some wire map testers. Explain how to connect the tone generator to the cable and select the appropriate tone for tracing.
Showcase their usefulness in locating specific cables within a complex wiring system, especially for hidden or bundled cables. They save time and effort compared to manually tracing cables visually.
They work best for identifying individual cables within a bundle, not necessarily pinpointing the exact path of the cable within a wall or conduit. Background noise in the environment can interfere with the audibility of the tone.

## Slide 44: Attenuation Issues
Loss of signal strength in networking cables or connections (measured in decibels (dB) or voltage)
Issues
Signal strength loss during transmission
Higher impedance, higher attenuation
Long cabling distance
Thin wire size
Environmental factors
Solutions
Shorten cable lengths
Use repeaters/extenders
Upgrade to high-quality cables
Measure and test signal attenuation at installation
Notes: Suggested Instructional Tip – Attenuation Issues
  Attenuation is the weakening of a signal as it travels through a cable. It's crucial to minimize attenuation to ensure reliable data transmission.
  Several factors contribute to attenuation, including:
  Cable length: Longer cables experience greater signal loss.
  Impedance: Higher impedance cables are more prone to attenuation.
  Wire size: Thinner wires offer less resistance to signal flow, leading to higher attenuation.
  Environmental factors: Extreme temperatures can impact signal strength.
Recommended Solutions:
  Shorten cable lengths: Whenever possible, use the shortest cable that meets your needs. This minimizes the distance the signal needs to travel and reduces attenuation.
  Use repeaters/extenders: For longer distances where signal strength becomes an issue, consider using repeaters or extenders. These devices amplify the signal, allowing it to travel further without significant degradation.
  Upgrade to high-quality cables: Invest in high-quality cables with lower impedance and thicker wire gauge. These cables are designed to minimize signal loss over longer distances.
  Measure and test signal attenuation at installation: Proactively test and document signal strength during cable installation. This establishes a baseline and helps identify potential issues early on.
Additional Points to Consider:
  Briefly explain the concept of signal-to-noise ratio (SNR) and how attenuation can negatively impact it. A strong SNR is crucial for error-free data transmission.
  Discuss the importance of using cables that meet the specific requirements of your application. For example, high-bandwidth applications might necessitate thicker cables or specific cable types with lower attenuation characteristics.
  If the slide includes visuals of different cable types, use them as a reference point while discussing cable quality upgrades.

## Slide 45: Interference Issues
Negative effects of electromagnetic, radio frequency, and electrostatic signals on cable transmissions
Issues
Electromagnetic interference (EMI)
Radio frequency interference (RFI)
Crosstalk from adjacent wires
Defective connectors/conductors
Solutions
Shielding techniques (foil/braided shields)
Use robust materials and strain relief
Compatibility testing
Systematic cable routing and organization
Notes: Suggested Instructional Tip – Interference Issues
Understanding Interference:
  Signal interference arises from external or internal sources, causing disruptions and data errors in cable transmissions.
  Common culprits include:
    Electromagnetic interference (EMI): Emissions from electrical devices like motors or power lines.
    Radio frequency interference (RFI): Signals from radio waves or wireless devices.
    Crosstalk: Electrical "crosstalk" between adjacent cables, where signals from one cable can couple into another.
    Defective connectors/conductors: Faulty connectors or damaged conductors within the cable itself.
Combating Interference:
  Shielding techniques: Utilize cables with foil or braided shields that act like barriers, deflecting external EMI and RFI.
  Systematic cable routing and organization: Maintain proper cable separation to minimize crosstalk. Avoid running power cables and signal cables in close proximity.
  Use robust materials and strain relief: Invest in cables with strong outer jackets and strain relief features to protect the conductors from physical damage that can create internal interference.
  Compatibility testing: For critical applications, consider compatibility testing between cables and network equipment to ensure they function optimally together and minimize signal disruption.
Additional Points to Consider:
  Briefly explain the concept of "grounded" cables and how proper grounding practices help mitigate EMI and improve signal quality.
  Discuss the importance of cable management strategies for maintaining organized cable layouts. This minimizes crosstalk and simplifies troubleshooting efforts.
  If the slide includes visuals of different cable shielding types, use them to illustrate the concept of shielding effectiveness.

## Slide 46: Crosstalk Issues
Near End Crosstalk (NEXT)
  Crosstalk at transmitter
  Caused by untwisting, faulty shields
Attenuation to Crosstalk Radio, Near End (ACRN)
  Insertion loss vs. NEXT
  High value: strong signal
Attenuation to Crosstalk Radio, Far End (ACRF)
  FEXT at recipient end
  Independent of link length
Power Sum
  Ensures cable suitability
  Interference from nearby cables
  Due to tight bundling, bad termination
  For Gigabit/10 GbE Ethernet
Alien Crosstalk
Interference caused by signal overlap cables
Notes: Suggested Instructional Tip – Crosstalk Issues
Crosstalk is not called out on the exam objectives document. So, you may prefer to skip this section in class.
Instructor Notes
  Near End Crosstalk (NEXT): Crosstalk measured at the transmitter end on the receive pairs.
  Causes: Often due to excessive untwisting of pairs or faulty bonding of shielded elements.
Attenuation to Crosstalk Ratio, Near End (ACRN): The difference between insertion loss and NEXT.
  Significance: Acts like a signal-to-noise ratio (SNR). A high ACRN value indicates a strong signal relative to noise; a value near zero suggests potential for high error rates.
Attenuation-to-Crosstalk Ratio, Far End (ACRF): Measures FEXT on the receive pairs at the recipient end.
  Importance: Provides a measure of cable performance that is independent of link length by comparing insertion loss to FEXT.
Power Sum: Relevant for Gigabit and 10 GbE Ethernet which use all four pairs.
  Measurement: Involves PSNEXT, PSACRN, and PSACRF calculations by energizing three pairs at a time to ensure cable suitability for high-speed applications.
Alien Crosstalk: Interference caused by signal traffic from adjacent cables.
  Common Causes: Can occur due to tightly cinched cable bundles or poorly terminated cabling.

## Slide 47: Crosstalk Issues: Solutions
Check for physical damage and improper installation
Avoid excessive untwisting
Use appropriate cable types and connectors
Ensure proper bundling
Notes: Suggested Instructional Tip - Crosstalk Issues: Solutions
Crosstalk is not called out on the exam objectives document. So, you may prefer to skip this section in class.

## Slide 48: Activity: Think About It
What are some symptoms of cabling issues?
Notes: Suggested Activity – Think About It
What are some symptoms of cabling issues?
Slow Internet Speeds
Random disconnections and reconnections
Connection timeouts.
Slowing down of applications
Lagging audio/video communication
Frequent drops or unstable network link

## Slide 49: Summary
Supporting Cabling and Physical Installations
Notes: Suggested Instructional Tips
Ask learners to summarize their key takeaways from this module
Conclude by going over main points on the next slide

## Slide 50: Main Points
Understand Cable Needs: Consider factors like interference and attenuation when choosing shielded copper or fiber optic cables
Proper Cable Preparation: Use appropriate tools for cable preparation and termination for connectors or punch-down blocks
Application-Specific Use: Ensure cables are used for their intended purpose to meet network requirements
Cable Testing: Verify cable integrity using appropriate testing tools to identify and troubleshoot faults​
Notes: Suggested Instructional Tip – Main Points
Reiterate the relevance of each point:​
Consider the factors that can affect the performance of network media, such as electromagnetic interference and attenuation and whether shielded copper or fiber optic cable will be required.
Use appropriate tools to prepare cables and terminate to either punch down blocks or to connectors.
Verify that cables are being used for their proper application.
Use cable testing tools to identify faults.